## Full operating licence
BLAXLAND SUSTAINABLE LEACHATE TREATMENT WETLANDS MONITORING DATA
Full Operating Licence EPL 10243
MONITORING POINT 3
Monitoring Frequency | Monthly
Method | Grab sample
Pollutant | Ammonia | BOD | Dissolved Cobalt | Dissolved Copper | Total Cyanide | Oil and Grease | Perfluorobutane-sulphonate (PFBS) | Perfluorohepta-noic acid (PFHpA) | Perfluorohexane-sulphonate (PFHxS) | Perfluorohexanoic acid (PFHxA) | Perfluoroocta-sulphonate (PFOS) | Perfluorooctanoic acid (PFOA) | pH | Total suspended solids | Bicarbonate | Nitrate | Nitrite | Total dissolved solids
Unit of measurement | (µg/L) | (mg/ L) | (µg/L) | (µg/L) | (µg/L) | (mg/L) | (µg/L) | (µg/L) | (µg/L) | (µg/L) | (µg/L) | (µg/L) | units | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L)
Discharge Limit | 910 | 50 | 1 | 40 | 4 | 10 | 1 | 1 | 1 | 1 | 0.07 | 1 | 6.5 - 8.5 | 25 | no limit | no limit | no limit | no limit
Licence Variation dated 06/06/2023 |  |  |  | 20
Date Sampled | [18 empty] | Date Received
2021-12-22 | 670 | 55 | 1 | 2 | <4 | <5 | 0.0431 | 0.0131 | 0.0427 | 0.0433 | 0.0309 | 0.0373 | 7.83 | 8 | 140 | 1.55 | 0.03 | 2780 | 2022-01-04
2022-01-07 | - | <2a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2022-01-13
2022-01-31 | 600 | 3 | 1 | <1 | <4 | <5 | 0.0306 | 0.0176 | 0.0517 | 0.0662 | 0.0346 | 0.0372 | 7.42 | 24 | 161 | 0.09 | <0.01 | 3140 | 2022-02-07
2022-02-22 | 290 | <2 | <1 | 4 | <4 | <5 | 0.063 | 0.0066 | 0.0533 | 0.0137 | 0.0294 | 0.0074 | 7.63 | -** | 144 | 5.73 | 0.08 | 3840 | 2022-03-01
2022-03-02 | - | - | - | - | - | - | - | - | - | - | - | - | - | <5 | - | - | - | - | 2022-03-02
2022-03-29 | 0.11 | <2 | <1 | 2 | <4 | <5 | 0.0131 | 0.0059 | 0.0276 | 0.0247 | 0.0244 | 0.0206 | 7.65 | 8 | 86 | 0.08 | <0.01 | 662 | 2022-04-06
2022-04-28 | 2680 | 2 | <1 | <1 | <4 | <5 | 0.0021 | 0.0026 | 0.0078 | 0.0104 | 0.0085 | 0.007 | 7.32 | 15 | 87 | 0.72 | 0.04 | 408 | 2022-05-05
2022-05-05 | 80a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2022-05-06
2022-05-31 | 80 | 28 | <1 | 6 | <4 | <5 | 0.0142 | 0.0054 | 0.0189 | 0.016 | 0.0156 | 0.0145 | 6.93 | <5 | 46 | 3.62 | 0.02 | 742 | 2022-06-08
2022-06-30 | 980 | 2 | <1 | 7 | <4 | <5 | 0.0154 | 0.0114 | 0.0339 | 0.0378 | 0.0188 | 0.0256 | 7.88 | <5 | 52 | 13.8 | 0.18 | 1730 | 2022-07-08
2022-07-05 | 930a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2022-07-06
2022-07-07 | 500a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2022-07-08
2022-07-28 | 8070 | 2 | <1 | 4 | <4 | <5 | 0.0384 | 0.0269 | 0.0541 | 0.073 | 0.0132 | 0.0288 | 6.9 | <5 | 48 | 29.6 | 0.45 | 4270 | 2022-08-05
2022-08-05 | 2,600a | - | - | - | - | - | - | - | - | - | - | - | 7.04 | - | - | - | - | - | 2022-08-08
2022-08-09 | 2,990a | - | - | - | - | - | - | - | - | - | - | - | 6.21 | - | - | - | - | - | 2022-08-10
2022-08-15 | 180a | - | - | - | - | - | - | - | - | - | - | - | 6.21a | - | - | - | - | - | 2022-08-16
2022-08-18 | - | - | - | - | - | - | - | - | - | - | - | - | 6.83a | - | - | - | - | - | 2022-08-18
2022-08-30 | 90 | 4 | <1 | 17 | <4 | <5 | 0.0099 | 0.0083 | 0.0259 | 0.0234 | 0.0302 | 0.0239 | 7.18 | <5 | 43 | 3.66 | 0.01 | 926 | 2022-09-06
2022-09-28 | 160 | <2 | <1 | 12 | <4 | <5 | 0.0126 | 0.0075 | 0.0272 | 0.0235 | 0.02 | 0.0242 | 7.23 | 17 | 40 | 11.2 | 0.13 | 1820 | 2022-10-07
2022-10-26 | 100 | <2 | <1 | 11 | <4 | <5 | 0.03 | 0.0084 | 0.0336 | 0.0292 | 0.0264 | 0.0328 | 7.36 | 8 | 64 | 11.8 | 0.05 | 1650 | 2022-11-02
2022-11-29 | 300 | <2 | <1 | 10 | <4 | <5 | 0.06 | 0.02 | 0.06 | 0.06 | 0.02 | 0.05 | 8.16 | 5 | 146 | 13.6 | 0.4 | 3650 | 2022-12-19
2022-12-30 | 240 | - | <1 | 9 | <4 | <5 | 0.0617 | 0.0213 | 0.0563 | 0.083 | 0.0243 | 0.0567 | - | <5 | 126 | - | - | 4400 | 2023-01-11
4/01/2023* | 410 | <2 | - | - | - | - | - | - | - | - | - | - | 8.08 | - | - | 7.97 | 0.41 | - | 2023-01-12
2023-01-24 | 340 | 2 | <1 | 6 | <4 | <5 | 0.06 | <0.02 | 0.07 | 0.08 | 0.03 | 0.05 | 7.67 | 5 | 128 | 10.8 | 0.1 | 4590 | 2023-02-02
2023-02-23 | 750 | 3 | <1 | 3 | <4 | <5 | 0.02 | <0.02 | 0.05 | 0.04 | 0.04 | 0.04 | 7.86 | <5 | 138 | 3.5 | 0.1 | 2890 | 2023-03-01
2023-03-22 | 940a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-03-27
2023-03-28 | 790a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-03-28
2023-03-29 | 1970 | <2 | <1 | 6 | <4 | <5 | 0.04 | <0.02 | 0.06 | 0.05 | 0.03 | 0.04 | 6.9 | <5 | 73 | 19.3 | 0.24 | 3410 | 2023-04-04
2023-04-14 | 1060a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-04-17
2023-04-17 | 460a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-04-18
2023-04-28 | 1380 | <2 | <1 | 6 | <4 | <5 | <0.02 | <0.02 | 0.01 | <0.02 | 0.01 | 0.02 | 7.67 | <5 | 60 | 2.25 | 0.25 | 687 | 2023-05-05
2023-05-08 | 860a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-05-08
2023-05-30 | 310 | 8 | <1 | 10 | <4 | <5 | 0.03 | <0.02 | 0.04 | 0.04 | 0.02 | 0.03 | 7.61 | 8 | 37 | 19.9 | 0.06 | 2230 | 2023-06-06
2023-06-27 | 1140 | 2 | <1 | 12 | <4 | <5 | 0.06 | <0.02 | 0.06 | 0.05 | 0.03 | 0.04 | 6.89 | 7 | 39 | 31.3 | 0.18 | 3100 | 2023-07-04
2023-07-07 | 1660a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-07-10
2023-07-11 | 240a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-07-12
2023-07-27 | 490 | <2 | <1 | 15 | <4 | 7 | 0.03 | <0.02 | 0.05 | 0.05 | 0.01 | 0.04 | 6.58 | <5 | 39 | 25.6 | 0.12 | 2640 | 2023-08-03
2023-08-31 | 300 | <2 | 1 | 12 | <4 | <5 | <0.02 | <0.02 | 0.04 | 0.03 | 0.02 | 0.04 | 7.4 | <5 | 92 | 6.1 | 0.11 | 1750 | 2023-09-06
2023-09-29 | 280 | 2 | <1 | 12 | <4 | <5 | <0.02 | <0.02 | 0.04 | 0.03 | 0.02 | 0.03 | 7.21 | 32 | 60 | 9.15 | 0.17 | 2150 | 2023-10-10
2023-10-12 | - | - | - | - | - | - | - | - | - | - | - | - | - | <5a | - | - | - | - | 2023-10-13
2023-10-23 | 510 | <2 | 1 | 7 | <4 | <5 | 0.02 | <0.02 | 0.05 | 0.05 | 0.02 | 0.03 | 7.2 | 12 | 124 | 3.72 | 0.16 | 2920 | 2023-10-31
2023-11-29 | 440 | 3 | <1 | 1 | <4 | <5 | <0.02 | <0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 7.74 | <5 | 112 | 4.01 | <0.01 | 2290 | 2023-12-06
2023-12-20 | 1590 | 3 | <1 | 3 | <4 | <5 | <0.02 | <0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 7.3 | 13 | 115 | 1.86 | 0.15 | 2360 | 29/12/2023 and 02/01/2023
2023-12-21 | 540a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2023-12-22
2024-01-24 | 1790 | <2 | <1 | <1 | <4 | <5 | 0.03 | <0.02 | 0.04 | 0.04 | 0.04 | 0.04 | 7.81 | 9 | 137 | 0.17 | 0.08 | 2250 | 2024-02-02
2024-02-05 | 1850a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2024-02-06
2024-02-07 | 1230a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2024-02-08
2024-02-13 | 1480a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2024-02-14
2024-02-16 | 840 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2024-02-19
2024-02-22 | 190 | 2 | <1 | 6 | <4 | <5 | <0.02 | <0.02 | 0.02 | <0.02 | 0.03 | 0.02 | 7.35 | 6 | 68 | 1.08 | 0.06 | 1520 | 2024-02-29
2024-03-28 | 1120 | <2 | <1 | 4 | <4 | <5 | 0.03 | <0.02 | 0.04 | 0.04 | 0.03 | 0.03 | 6.55 | 6 | 12 | 5.12 | 0.06 | 1990 | 2024-04-12
2024-04-10 | 200a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2024-04-11
2024-04-29 | 370 | 4 | <1 | 4 | <4 | <5 | 0.02 | <0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 7.34 | <5 | 105 | 1.12 | 0.06 | 2320 | 2024-05-06
2024-05-27 | 550 | 5 | <1 | 4 | <4 | <5 | <0.02 | <0.02 | 0.03 | <0.02 | 0.02 | 0.02 | 6.98 | 7 | 35 | 12.2 | 0.1 | 1400 | 2024-06-03
2024-06-27 | 1500 | <2 | <1 | 8 | <4 | <5 | 0.03 | 0.02 | 0.03 | 0.06 | 0.02 | 0.03 | 6.55 | <5 | 28 | 21.1 | 0.16 | 2010 | 2024-07-04
2024-07-04 | 960a | - | - | - | - | - | - | - | - | - | - | - | 6.34 | - | - | - | - | - | 2024-07-05
2024-07-08 | 1480a | - | - | - | - | - | - | - | - | - | - | - | 6.41a | - | - | - | - | - | 2024-07-09
2024-07-12 | 1620a | - | - | - | - | - | - | - | - | - | - | - | 7.24a | - | - | - | - | - | 2024-07-15
2024-07-16 | 150a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2024-07-17
2024-07-24 | 1000 | 4 | <1 | 15 | 3.51 | <5 | 0.02 | <0.02 | 0.04 | <0.02 | 0.02 | 0.03 | 6.02 | <5 | 19 | 13.4 | 0.13 | 1320 | 2024-07-30
2024-07-31 | 780a | - | - | - | - | - | - | - | - | - | - | - | 7.19a | - | - | - | - | - | 2024-08-05
2024-08-28 | 120 | 10 | <1 | 8 | <4 | <5 | <0.02 | <0.02 | 0.03 | 0.02 | 0.03 | 0.02 | 6.81 | 39 | 33 | 10.5 | 0.07 | 1210 | 2024-09-04
2024-09-05 | - | - | - | - | - | - | - | - | - | - | - | - | - | <5a | - | - | - | - | 2024-09-06
2024-09-23 | 200 | <2 | <1 | <1 | <4 | <5 | <0.02 | <0.02 | 0.02 | <0.02 | 0.02 | 0.02 | 6.88 | 14 | 47 | 9.67 |  | 1430
2024-10-30 | 180 | 4 | <1 | 6 | <4 | <5 | 0.02 | <0.02 | 0.03 | 0.03 | 0.02 | 0.03 | 7.62 | <5 | 94 | 5.8 | 0.15 | 1870 | 2024-11-06
2024-11-28 | 340 | 5 | <1 | 3 | <4 | <5 | <0.02 | <0.02 | 0.04 | 0.04 | 0.03 | 0.03 | 7.44 | 6 | 132 | 0.22 | 0.03 | 2240 | 2024-12-05
2024-12-18 | 720 | 3 | 1 | 4 | <4 | 8 | <0.02 | <0.02 | 0.03 | <0.02 | 0.04 | 0.02 | 7.63 | <5 | 130 | 0.02 | 0.02 | 1040 | 2024-12-24
2025-01-31 | 1430 | <2 | <1 | <1 | <4 | 8 | 0.02 | <0.02 | 0.04 | 0.04 | 0.03 | 0.04 | 7.45 | <5 | 150 | 0.75 | 0.01 | 2440 | 2025-02-07
2025-02-11 | 2301a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-02-12
2025-02-12 | 1450a | 3 | <1 | 3 | <4 | <5 | 0.02 | <0.02 | 0.05 | 0.04 | 0.01 | 0.04 | 6.87 | <5 | 82 | 5.27 | 0.14 | 3340 | 2025-02-18
2025-02-17 | 250 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-02-18
2025-03-19 | 330 | 4 | 1 | 8 | <4 | <5 | 0.03 | <0.02 | 0.04 | 0.04 | 0.01 | 0.03 | 7.05 | <5 | 88 | 7.54 | 0.16 | 2660 | 2025-03-26
2025-04-30 | 2930 | 4 | 4 | 8 | <4 | <5 | <0.02 | <0.02 | 0.03 | 0.04 | 0.02 | 0.03 | 7.22 | <5 | 79 | 10.5 | 0.26 | 2820 | 2025-05-06
2025-05-08 | 5305a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-05-09
2025-05-09 | - | - | 2a | 9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-05-12
2025-05-13 | 1207a | - | 1 | - | - | - | - | - | - | - | - | - | 7.24 | - | - | 29.7 | 0.64 | - | 2025-05-14
2025-05-15 | 2207a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-05-16
2025-05-19 | 204a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-05-20
2025-05-28 | 4060 | 7 | 2 | 15 | <4 | <5 | <0.02 | <0.02 | 0.03 | 0.03 | 0.01 | 0.04 | 7.17 | 13 | 44 | 13.7 | 0.26 | 2580 | 2025-06-06
2025-06-05 | 3160a | - | <1a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-06-06
2025-06-10 | 440a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-06-10
2025-06-19 | 50 | 3 | 1 | 11 | <4 | <5 | 0.04 | <0.02 | 0.03 | 0.04 | 0.01 | 0.02 | 6.99 | 8 | 36 | 33.1 | 0.04 | 3420 | 2025-06-30
2025-07-28 | 140 | <2 | 1 | 14 | <4 | <5 | 0.04 | <0.02 | 0.04 | 0.05 | 0.01 | 0.04 | 6.63 | <5 | 21 | 28.5 | 0.12 | 3160 | 2025-08-04
2025-08-27 | 90 | <2 | <1 | 13 | <4 | <5 | <0.02 | <0.02 | 0.04 | <0.02 | 0.02 | 0.04 | 6.8 | <5 | 44 | 13.6 | 0.04 | 1690 | 2025-09-04
2025-09-25 | 150 | 3 | <1 | 13 | <4 | <5 | 0.03 | <0.02 | 0.05 | 0.04 | 0.02 | 0.04 | 6.75 | <5 | 38 | 35.2 | 0.09 | 2910 | 2025-10-02
2025-10-22 | 190 | 2 | <1 | 10 | <4 | <5 | <0.02 | <0.02 | 0.05 | 0.03 | 0.02 | 0.03 | 6.51 | <5 | 70 | 18.7 | 0.1 | 2360 | 2025-11-13
2025-11-19 | 160a | - | - | - | - | - | - | - | - | - | - | - | 7.64 | - | - | 0.45 | 0.03 | -
2025-11-26 | 190 | <2 | 4 | 24 | <4 | <5 | 0.07 | 0.03 | 0.05 | 0.11 | 0.02 | 0.03 | 6.6 | <5 | 41 | 30.5 | 0.37 | 8530
2025-12-03 | - | - | 2a | 19a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2025-12-09
2025-12-11 | 50 | <2 | <1 | 15 | <4 | <5 | 0.08 | 0.02 | 0.05 | 0.1 | 0.02 | 0.03 | 6.27 | <5 | 42 | 29.2 | 0.02 | 11200 | 2025-12-22
2025-12-17 | - | - | - | - | - | - | - | - | - | - | - | - | 6.85a | - | - | - | - | - | 2025-12-22
2025-12-22 | 5630a | - | - | - | - | - | - | - | - | - | - | - | 7.13a | - | - | 20.2a | 0.4a | -
2025-12-30 | 4200a | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2026-01-05 | 180a | - | - | - | - | - | - | - | - | - | - | - | 7.33a | - | - | 15.8a | 0.65a | -
2026-01-19 | 200 | - | - | - | - | - | - | - | - | - | - | - | 7.19 | - | - | 5.72 | 0.04 | - | 2026-01-28
2026-01-28 | 50 | 3 | <1 | 27a | <4 | <5 | 0.03 | <0.02 | 0.06 | 0.04 | 0.03 | 0.04 | 7.71 | <5 | 96 | 10.4 | 0.3 | 3530
2026-02-06 | - | - | - | 20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Resampling
2026-02-13 | 60 | [11 empty] | 7.52 | - | - | 14.6 | 0.05 | -
2026-02-25 | 200 | 2 | 5 | 26 | <4 | 6 | 0.03 | 0.02 | 0.06 | 0.07 | 0.05 | 0.08 | 7.42 | <5 | 100 | 0.37 | 0.03 | 3140
2026-03-05 |  |  | 3a | 13a | [14 empty] | Resampling
2026-03-09 |  |  | <1a | [15 empty] | Resampling
2026-03-25 | 700 | 3 | 2 | 3 | <4 | <5 | 0.03 | <0.02 | 0.04 | 0.04 | 0.03 | 0.04 | 6.98 | <5 | 106 | 0.02 | <0.01 | 2660
2026-04-02 |  |  | 2a | [15 empty] | Resampling
2026-04-08 | 30 |  | 1 | [9 empty] | 7.43 |  |  | 2.25 | 0.03 |  | 2024-04-10
* Laboratory error - samples not analysed witihn holding times. Additional sampes taken
Units | Description | [10 empty] | Licensee Name |  | Sydney Olympic Park Authority.
pH units | Measurement of pH on a scale of 0 to 14, utilising the log10 of free hydrogen ions in solution. | [10 empty] | Licensee Address |  | Locked Bag 3, SYDNEY OLYMPIC PARK, NSW 2127
mg per L | Milligrams per Litre - the amount, in milligrams, of a pollutant per litre of substrate measured. | [10 empty] | Location of Monitoring Point 3 |  | Pump well at outlet of discharge pipes located at northern end of treatment ponds BLAX1 and BLAX2
µg per L | Micrograms per Litre - the amount in micrograms, of a pollutant per litre of substrate measured
a | Additional sampling in accordance with licence requirements
** | Sample taken but was not representative. Resampled on 02/03/2022 to confirm Total Suspended Solids at Monitoring Point 3 were compliant.
The Licence 10243 can be viewed in full on the NSW EPA website:
https://apps.epa.nsw.gov.au/prpoeoapp/Detail.aspx?instid=10243&id=10243&option=licence&searchrange=licence&range=POEO%20licence&prp=no&status=Issued
NOTE: This document is available at https://www.sydneyolympicpark.com.au/Environment/Environmental-Monitoring-Data and is uncontrolled once downloaded and/or printed.

## POP testing
BLAXLAND SUSTAINABLE LEACHATE TREATMENT WETLANDS MONITORING DATA
ENVIRONMENTAL PROTECTION LICENCE 10243
MONITORING POINT 3
Monitoring Frequency | Special Frequency 1
Method | Grab sample.
Pollutant | Arsenic (III) | Arsenic (V) | Cadmium | Hexavalent Chromium | Trivalent Chromium | Cobalt | Copper | Lead | Nickel | Zinc | Ammonia | Total Anions | Total Cations | BOD | Cyanide | Oil and Grease | pH | Total Suspended Solids | Benzene | Total Petroleum Hydrocarbons C6-C9 Fraction | Total Petroleum Hydrocarbons C10-C14 Fraction | Total Petroleum Hydrocarbons C15-C28 Fraction | Bisphenol-A | Diphenylamine | Molinate | 1,2,3,4,6,7,8-Heptachlorodibenzo-furan (-HpCDF) | 1,2,3,4,6,7,8-Heptachlorodibenzo-p-dioxin (-HpCDD) | 1,2,3,4,7,8-Hexachlorodi-benzofuran (-HxCDF) | Octachlorodi-benzo-p-dioxin (OCDD) | 2,2',3,3',4,4',5,5',6,6'-Decabromodiphenyl ether | 2,2',3,3',4,4',5,5',6-Nonabromodi-phenyl ether | 2,2',3,3',4,4',5,6,6'-Nonabromodi-phenyl ether | 2,2',3,3',4,5,5',6,6'-Nonabromodi-phenyl ether | Perfluorobutane-sulphonate (PFBS) | Perfluorohepta-noic acid (PFHpA) | Perfluorohexane-sulphonate (PFHxS) | Perfluorohexa-noic acid (PFHxA) | Perfluoroocta-sulphonate (PFOS) | Perfluorooctanoic acid (PFOA)
Unit of measurement | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | meq/L | meq/L | (mg per L) | (µg per L) | (mg per L) | (pH units) | (mg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (pg per kg) | (pg per kg) | (pg per kg) | (pg per kg) | (ng per kg) | (ng per kg) | (ng per kg) | (ng per kg) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L) | (µg per L)
100 percentile concentration limit | 25 | 45 | 0.7 | 4.4 | 27.4 | 1 | 1.3 | 4.4 | 70 | 150 | 910 | no limit | no limit | 50 | 4 | 10 | 6.5-8.5 | 25 | 500 | 20 | 50 | 100 | 31.5 | 8 | 3.4 | ND (10) | ND (10) | ND (5) | ND (100) | ND (10) | ND (0.6) | ND (0.6) | ND (0.3) | ND (0.02) | ND (0.02) | ND (0.02) | ND (0.02) | ND (0.02) | ND (0.02)
New limit | [6 empty] | 13a | [18 empty] | 10pg/Lb | [7 empty] | 1c | 1c | 1c | 1c |  | 1c
New limit | [6 empty] | 40aa
Date Sampled | [39 empty] | Date Received | Date Published
2014-06-26 | <1 | 1 | <0.05 | <1 | <1 | 0.4 | 7.7 | <0.1 | 0.8 | <1 | 320 | 30.6 | 31.9 | <2 | <4 | <5 | 7.67 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | <1.1 | 3.8 | <0.6 | 36 | <0.06 | <0.007 | <0.006 | <0.006 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 2014-07-08 | 2014-07-15
1.05
2014-07-10 | - | - | - | - | - | - | 13.1* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014-07-17 | 2014-07-30
2014-07-17 | - | - | - | - | - | - | 16.5* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014-07-23 | 2014-07-30
2014-07-24 | - | - | - | - | - | - | 18.1* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014-07-30 | 2014-08-02
2014-07-31 | - | - | - | - | - | - | 21.5* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014-08-05 | 2014-08-08
2014-08-14 | - | - | - | - | - | - | 20.0* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014-08-21 | 2014-09-02
2014-08-21 | - | - | - | - | - | - | 8.2* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014-08-26 | 2014-09-02
2014-09-04 | <1 | <1 | <0.05 | <1 | <1 | 0.5 | 12 | <0.1 | 0.7 | 1 | 40 | 30.4 | 28.8 | <2 | <4 | <5 | 7.91 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 0.82 |  |  |  | <0.2 | <0.01 | <0.007 | <0.008 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 2014-09-16 | 2014-10-31
2014-11-06 | <1 | <1 | <0.05 | <1 | <1 | 0.7 | 10.8 | <0.1 | 1.4 | 3 | 180 | 36.1 | 50.3 | <2 | <4 | <5 | 7.74 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 1.45 |  |  |  | <0.4 | <0.02 | <0.02 | <0.005 | <0.02 | <0.02 | <0.02 | 0.02 | <0.02 | <0.02 | 2014-11-18 | 2014-11-21
2014-11-24 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | 0.09* | - | - | 2014-11-26 | 2014-12-04
2014-11-27 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | 0.13* | - | - | 2014-12-03 | 2014-12-04
2014-12-04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | [5 empty] | <0.02* | - | - | 2014-12-08 | 2014-12-09
2014-12-15 | <1 | <1 | <0.05 | <1 | <1 | 0.7 | 3.4 | <0.1 | 0.9 | 1 | 300 | 20.9 | 20.5 | <2 | <4 | <5 | 7.49 | 10 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 2.14 |  |  |  | <0.1 | <0.01 | <0.01 | <0.01 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 2015-01-06 | 2015-01-12
2015-02-16 | <1 | <1 | <0.05 | <1 | <1 | 1.2 | 18 | <0.1 | 1 | 3 | 1340 | 50.8 | 56.6 | 4 | <4 | <5 | 7.4 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 1.77 |  |  |  | <0.3 | <0.03 | <0.03 | <0.03 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | 2015-03-02 | 2015-03-12
2015-02-24 | - | - | - | - | - | 1.3* | 22.4* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-02-27 | 2015-03-12
2015-02-26 | - | - | - | - | - | - | - | - | - | - | 120* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-03-03 | 2015-03-12
2015-03-03 | - | - | - | - | - | 0.7* | 24.0* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-03-09 | 2015-03-12
2015-03-10 | - | - | - | - | - | - | 20.0* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-03-16 | 2015-04-01
2015-03-16 | - | - | - | - | - | - | 15.0* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-03-19 | 2015-04-01
2015-03-23 | - | - | - | - | - | - | 8.6* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-03-26 | 2015-04-01
2015-04-02 | <1 | <1 | <0.05 | <1 | <1 | 0.7 | 10.1 | <0.1 | 1.1 | 1 | 900 | 57.2 | 56.5 | <2 | <4 | <5 | 7.65 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 2.77 |  |  |  | <0.2 | <0.04 | <0.03 | <0.03 | 0.02 | <0.02 | 0.03 | 0.03 | <0.02 | <0.02 | 2015-04-17 | 2015-04-20
2015-04-15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | 0.05* | - | 0.09* | 0.04* | - | - | 2015-04-17 | 2015-04-20
2015-04-21 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | <0.02* | - | <0.02* | <0.02* | - | - | 2015-04-23 | 2015-04-28
2015-05-07 | <1 | <1 | <0.05 | <1 | <1 | 0.5 | 9.8 | <0.1 | 1 | <1.0 | <10 | 30.6 | 36.3 | 3 | <4 | <5 | 7.64 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 3.36 |  |  |  | <0.1 | <0.04 | <0.02 | <0.03 | <0.02 | <0.02 | <0.02 | 0.06 | <0.02 | <0.02 | 2015-05-20 | 2015-05-29
2015-05-18 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | 0.12* | - | - | 2015-05-20 | 2015-05-29
2015-05-21 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | 0.13* | - | - | 2015-05-26 | 2015-05-29
2015-05-25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | 0.05* | - | - | 2015-05-28 | 2015-05-29
2015-06-02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | 0.04* | - | - | 2015-06-05 | 2015-06-16
2015-06-09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | 0.08* | - | - | 2015-06-11 | 2015-06-16
2015-06-19 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | <0.02* | - | - | 2015-06-24 | 2015-06-25
2015-06-29 | <1 | <1 | <0.05 | 2 | <1 | 0.6 | 11.4 | <0.1 | 1.3 | <1.0 | 3630 | 31.6 | 34.4 | <2 | <4 | 11 | 7.64 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 0.95 |  |  |  | <0.3 | <0.04 | <0.04 | <0.03 | <0.02 | <0.02 | 0.05 | 0.05 | <0.02 | 0.02 | 2015-07-13 | 2015-07-15
2015-07-03 | - | - | - | - | - | - | - | - | - | - | 20* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-07-03 | 2015-07-15
2015-07-13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | 0.04* | 0.04* | - | 0.02* | 2015-07-15 | 2015-07-15
2015-07-15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | <5* | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | 0.04* | <0.02* | - | <0.02* | 2015-07-17 | 2015-07-27
2015-07-20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | 0.02* | - | - | - | 2015-07-22 | 2015-07-27
2015-07-24 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | 0.04* | - | - | - | 2015-07-27 | 2015-07-27
2015-07-30 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | 0.02* | - | - | - | 2015-07-31 | 2015-08-11
2015-08-06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | 0.02* | - | - | - | 2015-08-11 | 2015-08-11
2015-08-13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | <0.02 | - | - | - | 2015-08-17 | 2015-08-25
2015-09-10 | <1 | <1 | <0.05 | <1 | <1 | 0.7 | 17 | <0.1 | 1.3 | 3 | 190 | 38.5 | 47 | <2 | <4 | 12 | 7.07 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 2.18 |  |  |  | <0.1 | <0.01 | <0.02 | <0.01 | <0.02 | <0.02 | 0.05 | 0.1 | <0.02 | 0.03 | 2015-09-28 | 2015-09-30
2015-09-21 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | <5* | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | 2015-09-21 | 2015-09-30
2016-06-30 | <1 | <1 | <0.2 | <1 | <10 | 0.9 | 35 | <0.2 | 1.7 | 12 | 4.27 | 34.7 | 39 | <2 | <4 | <5 | 6.85 | <5 | <1 | <20 | <50 | <100 | <0.05 | <4 | <0.1 | 3.13 |  |  |  | <1 | <0.08 | <0.07 | <0.03 | <0.02 | <0.02 | 0.04 | 0.04 | 0.02 | <0.02 | 2016-07-12 | 2016-07-19
2016-07-11 | - | - | - | - | - | - | - | - | - | - | 0.06* | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | 0.02* | - | 2016-07-13
2016-07-14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | <0.01* | - | 2016-07-18
Units | Description | [14 empty] | Licensee Name | Sydney Olympic Park Authority.
pH units | Measurement of pH on a scale of 0 to 14, utilising the log10 of free hydrogen ions in solution. | [14 empty] | Licensee Address | Locked Bag 3, SYDNEY OLYMPIC PARK, NSW 2127
mg per L | Milligrams per Litre - the amount, in milligrams, of a pollutant per litre of substrate measured. | [14 empty] | Location of Monitoring Point 3 | Pump well at outlet of discharge pipes located at northern end of treatment ponds BLAX1 and BLAX2
µg per L | Micrograms per Litre - the amount in micrograms, of a pollutant per litre of substrate measured
ng per kg | Nanograms per Kilogram - the amount, in milligrams, of a pollutant per kilogram of substrate measured.
pg per kg | Picograms per Kilogram - the amount, in milligrams, of a pollutant per kilogram of substrate measured.
meq/L | Milliequivalents per Litre - the measured amount of a solute per litre of a solvent.
* | Additional sampling in accordance with licence requirements
a | Copper 100 percentile concentration limit increased to 13µg/L effective as of 14 August 2014.
b | Original limits based on mass values were revised in line with World Health Organisation trigger limits which are reported as WHO toxic equivalency concentration limits. WHO-TEQ2 for the suite of dioxins required to be monitored by the licence of 10pg/L effective as of 22 October 2014.
c | Non detect limit increased to a 100 percentile concentration limit of 1µg/L effective as of 31 August 2015.
The Licence 10243 can be viewed in full on the NSW EPA website:
http://www.epa.nsw.gov.au/prpoeoapp/Detail.aspx?id=10243&option=licence&searchrange=licence&range=POEOlicence&prp=no&status=Issued
NOTE: This document is available at www.sopa.nsw.gov.au and is uncontrolled once downloaded and/or printed.